## Thermistors
Vendor | Model/Type | Signal | Base Resis | Input Config | Output Range | File | ZIP | Note | 0 F / -18 C | 32 F / 0 C | 77 F / 25 C | 100 F / 38 C | mV / deg
ACI | A/20K | Passive | 20K | 10K pullup | -40 to 116 C | aci-20k_Celsius.csv | 20k-aci.zip | Curve 20 | 193390 | 70160 | 20000 | 11245 | 27.8889 | Note: The mv/deg column is normalized to a 3V reference voltage at 72 F (22.2 C)
ACI | A/20K | Passive | 20K | 10K pullup | -40 to 240 F | aci-20k_Fahrenheit.csv | 20k-aci.zip | Curve 20 | 193390 | 70160 | 20000 | 11245 | 50.2
BAPI | 1.8K | Passive | 1.8K | 1K pullup | -55 to 150 C | bapi-1.8k_Celsius.csv | 1.8k-bapi.zip | Various vendors | 11168 | 4962 | 1800 | 1133 | 14.1111
BAPI | 1.8K | Passive | 1.8K | 1K pullup | -67 to 302 F | bapi-1.8k_Fahrenheit.csv | 1.8k-bapi.zip | Various vendors | 11168 | 4962 | 1800 | 1133 | 25.4
BAPI | 10K Type 4 | Passive | 10K | 10K pullup | -32 to 77 C | bapi-10k-4_Celsius.csv | 10k-4-bapi.zip |  | 60803 | 27348 | 10000 | 6314 | 15.7778
BAPI | 10K Type 4 | Passive | 10K | 10K pullup | -25 to 170 F | bapi-10k-4_Fahrenheit.csv | 10k-4-bapi.zip |  | 60803 | 27348 | 10000 | 6314 | 28.4
Barber Coleman | TS-902 | Passive | 10K | 10K pullup | -40 to 121 C | BarberColeman-TS902X-11shunt_Celsius.csv | 10k-with-11k-shunt-BarberColeman-TS902X.zip |  | 9527 | 8012 | 5238 | 3893 | 15.1667
Barber Coleman | TS-902 | Passive | 10K | 10K pullup | -40 to 250 F | BarberColeman-TS902X-11shunt_Fahrenheit.csv | 10k-with-11k-shunt-BarberColeman-TS902X.zip |  | 9527 | 8012 | 5238 | 3893 | 27.3
Carel | Type Z | Passive | 10K | 10K pullup | -40 to 121 C | distech-z-10k_Celsius.csv | 10k-distech-z.zip | Type Z 10K NTC | 60620 | 27197 | 10000 | 6277 | 0
Carel | Type Z | Passive | 10K | 10K pullup | -40 to 250 F | distech-z-10k_Fahrenheit.csv | 10k-distech-z.zip | Type Z 10K NTC | 60620 | 27197 | 10000 | 6277
Carrier | Type 46A | Passive | 5K | 10K pullup | -32 to 107 C | carrier-5k_use-10k-pullup_Celsius.csv | 5k-Carrier-Type46A.zip |  | 42679 | 16346 | 4976 | 2898 | 31.2778
Carrier | Type 46A | Passive | 5K | 10K pullup | -25 to 225 F | carrier-5k_use-10k-pullup_Fahrenheit.csv | 5k-Carrier-Type46A.zip |  | 42679 | 16346 | 4976 | 2898 | 56.3
Daikin | "20 K" | Passive | 20K | 10K pullup | -20 to 80 C | daikin-20k_Celsius.csv | 20k-daikin.zip |  | 174520 | 65294 | 20000 | 11740 | 28.2778
Daikin | "20 K" | Passive | 20K | 10K pullup | -4 to 176 C | daikin-20k_Fahrenheit.csv | 20k-daikin.zip |  | 174520 | 65294 | 20000 | 11740 | 50.9
Distech | Type Z | Passive | 10K | 10K pullup | -40 to 121 C | distech-z-10k_Celsius.csv | 10k-distech-z.zip | Type Z 10K NTC | 60620 | 27197 | 10000 | 6277 | 0
Distech | Type Z | Passive | 10K | 10K pullup | -40 to 250 F | distech-z-10k_Fahrenheit.csv | 10k-distech-z.zip | Type Z 10K NTC | 60620 | 27197 | 10000 | 6277
Honeywell | "20 K" | Passive | 20K | 10K pullup | -40 to 116 C | aci-20k_Celsius.csv | 20k-aci.zip | Curve 20 | 193390 | 70160 | 20000 | 11245 | 0
Honeywell | "20 K" | Passive | 20K | 10K pullup | -40 to 240 F | aci-20k_Fahrenheit.csv | 20k-aci.zip | Curve 20 | 193390 | 70160 | 20000 | 11245
Honeywell | C7041 | Passive | 20K | 10K pullup | -40 to 189 C | honeywell-c7041-20k_Celsius.csv | 20k-honeywell-c7041.zip | Type 17 | 194800 | 70600 | 20000 | 11245 | 30.1667
Honeywell | C7041 | Passive | 20K | 10K pullup | -40 to 300 F | honeywell-c7041-20k_Fahrenheit.csv | 20k-honeywell-c7041.zip | Type 17 | 194800 | 70600 | 20000 | 11245 | 54.3
TAC | TS-902 | Passive | 10K | 10K pullup | -40 to 121 C | BarberColeman-TS902X-11shunt_Celsius.csv | 10k-with-11k-shunt-BarberColeman-TS902X.zip |  | 9527 | 8012 | 5238 | 3893 | 15.1667
TAC | TS-902 | Passive | 10K | 10K pullup | -40 to 250 F | BarberColeman-TS902X-11shunt_Fahrenheit.csv | 10k-with-11k-shunt-BarberColeman-TS902X.zip |  | 9527 | 8012 | 5238 | 3893 | 27.3

## Potentiometers
Type | Vendor | Model | Signal | Input Config | Output Range | File | ZIP | Note
10K Potentiometer | KMC | STE-6014/17/18/19/20 | Passive | 10K pullup | 0.0 to 1.0 (no units) | 10k-pot_0-to-1_linear.csv | 10k-STE-Potentiometer.zip | Good for setpoints - all positive numbers
10K Potentiometer | KMC | STE-6014/17/18/19/20 | Passive | 10K pullup | -1.0 to 1.0 (no units) | 10k-pot_-1-to-1_linear.csv | 10k-STE-Potentiometer.zip | Use for temperature deltas - positive and negative numbers